## Sheet1
Example dwelling HIU and space heating commissioning check list (indirect HIU with radiators)
HIU model |  |  | KEY | Yellow - designer to complete prior to commissioning
HIU serial number |  |  |  | Grey - complete during commissioning
Building visited |  |  | Heat meter serial No.
Flat number |  |  | kWh on meter
Engineer |  |  | Date
Start time |  |  | End time
Action 1: Initial checks |  | Design value | confirmation
Flushing bypass closed |  | n/a | (tick)
Strainer clean |  | n/a | (tick)
DH primary supply up to temperature |  | [70 C +/- 3C | (tick) | Run DHW to get hot DH flow to HIU
Check heat meter working, no errors, no negative flows. Not negative dT when HIU supplying heat |  |  | (tick) | If not OK stop commissioning process
Action 2: Turn heating on, check flow into top of radiator whilst heating up then check valve setting and that no air in radiators
Set radiator valves | confirm heating flow in at top of radiator and return out of bottom | pre-setting value | confirm setting and that lock shield fully open | confirm no air in radiator
Hall | Yes / No | [1] | Yes / No | Yes / No
Living room | Yes / No | [6] | Yes / No | Yes / No
Kitchen | Yes / No | [3] | Yes / No | Yes / No
Bedroom 1 | Yes / No | [2] | Yes / No | Yes / No
etc. | Yes / No |  | Yes / No | Yes / No
Towel rail return temperature limiter | Yes / No | [3] | Yes / No | Yes / No
NOTE (may be different setting method for radiator with no TRV)
Secondary system pressure |  | [1.5bar] | confirm
Pump speed setting |  | [2] | confirm pump set
Action 3: Confirm space heating system commissioned to achieve design objectives,
Put clamp on thermometer on secondary flow and return pipes next to HIU, all TRVs set to highest temperature and room thermostat to maximum. Monitor temperatures until stabilised (30 minutes) then take measurements below. Or use heat meter kW and measure
| design value | tolerance | value achieved | meets criteria?
Tertiary flow temperature | [60] | [+/- 4C] |  | Yes / No
Recommended starting setting for space heat control valve | [2.5]
Tertiary return temperature | [40C] | [-10 / +5 C] |  | Yes / No (if criteria not met need to check individual radiator return temperatures)
Secondary return temperature from heat meter | [41C] | [-10 / +5 C]
Heat consumption kW (option?) | [4kW] | [+/- 1kW] |  | Yes / No
OR (instead of 3 lines above)
Calculate secondary flow rate based on kW from heat meter and measured tertiary dT with all radiators fully on | [0.2 m3/hr] | [+/- 0.04 m3/hr] |  | Yes / No
Confirm room thermostat turns heating off |  |  |  | Yes / No
Action 4 - Set up DHW
Can this be done whilst heating is stabilising ? The designer should test if this is possible. No if HIU has DHW priority
Recommended starting setting for DHW control valve | [2]
| design value | tolerance | value achieved | meets criteria?
DHW temperature | [50C] | [+5C /-0 C] |  | Yes / No
CWS temperature | n/a | n/a |  | n/a
Secondary return temperature from heat meter | [8C above CWS supply temperature] | [-8 / +5 C] |  | Yes / No
Power output - check kitchen tap output is between 10 - 20kW | confirm output - needs to be between 10 -20 kW to use return temperature data from HIU test as basis for design return temperature |  |  | Yes / No
DHW temperature at kitchen tap is 50C within one minute | [50C] | [+5C /-0 C] |  | Yes / No
(OPTIONAL) Action 5 - Use AMR data to confirm acceptable HIU standby return temperatures and heat losses
To be assessed after in-flat commissioning (as on many HIUs the DHW set point impacts upon the standby temperature settings)
Use values averaged over a long period when no DHW or space heating use)
| design value | tolerance | value achieved | meets criteria?
DH return temperature | [50C] | [ +5 C] |  | Yes / No
HIU standby heat loss | [70 Watts] | [+20 W] |  | Yes / No
Other possible checks
- Check operation of prepayment valve if fitted
- It is advisable that heating programmers are not all set for the heating to come on in all flats at the same time
- Present graph of high frequency AMR data for the duration of commissioning process to show at least one meter read during DHW draw off, and a number of meters read showing that space heating has stabilised, and the subsequent performance is satisfactory
- State some settings for the thermostat and TRVs to be set to, e.g. for frost protection