## Sheet1
This sheet is for estimating the effects of erosion within pipework based on an acceptable continuous pipe velocity of 1m/s.
Rates of erosion are based on the kinetic energy of water and particles.
Effects are weighted by time.
Peak DHW Output | 50 | kw
Litres of water per day @55C | 240 | litres | [5 empty] | Peak Velocity |  | Minutes Velocity Squared |  |  | Peak DHW Power (kW) at velocity (m/s)
Peak Heating Output | 5 | kW | OK | Diameter | Wall | Bore | Area | DHW | CH | DHW | CH | Total | 0.5 | 0.75 | 1 | 1.5 | 2 | 2.5 | 3 | 4 | 6 | 8
Primary Flow Temperature | 70 | C
Return Temperature, DHW | 25 | C | 0 | 6 | 0.7 | 4.6 | 16.619 | 15.9185 | 2.3878 | 3831.403 | 8210.1493 | 12041.5523 | 1.5705 | 2.3557 | 3.141 | 4.7115 | 6.282 | 7.8525 | 9.423 | 12.564 | 18.846 | 25.1279
Return Temperature, CH | 40 | C | 0 | 8 | 0.7 | 6.6 | 34.2119 | 7.7327 | 1.1599 | 904.0937 | 1937.3435 | 2841.4372 | 3.233 | 4.8495 | 6.4661 | 9.6991 | 12.9321 | 16.1651 | 19.3982 | 25.8642 | 38.7963 | 51.7284
Acceptable constant velocity | 1 | m/s | 1 | 10 | 0.7 | 8.6 | 58.088 | 4.5543 | 0.68315 | 313.6139 | 672.0299 | 985.6438 | 5.4893 | 8.234 | 10.9786 | 16.4679 | 21.9573 | 27.4466 | 32.9359 | 43.9145 | 65.8718 | 87.8291
|  |  | 1 | 12 | 0.7 | 10.6 | 88.2473 | 2.9978 | 0.44967 | 135.8832 | 291.1782 | 427.0614 | 8.3394 | 12.509 | 16.6787 | 25.0181 | 33.3575 | 41.6968 | 50.0362 | 66.7149 | 100.0724 | 133.4299
Litres of water per day @40C | 360 | litres | 1 | 15 | 0.7 | 13.6 | 145.2671 | 1.8211 | 0.27317 | 50.1457 | 107.455 | 157.6007 | 13.7277 | 20.5916 | 27.4555 | 41.1832 | 54.911 | 68.6387 | 82.3665 | 109.8219 | 164.7329 | 219.6439
Minutes per day at peak DHW load | 15.12 | minutes | 1 | 22 | 0.7 | 20.6 | 333.2913 | 0.79375 | 0.11906 | 9.5262 | 20.4133 | 29.9395 | 31.496 | 47.244 | 62.9921 | 94.4881 | 125.9841 | 157.4801 | 188.9762 | 251.9682 | 377.9523 | 503.9364
Percentage of time at peak | 1.05% |  | 0 | 28 | 1.7 | 24.6 | 475.2912 | 0.55661 | 0.083491 | 4.6843 | 10.0379 | 14.7222 | 44.915 | 67.3725 | 89.83 | 134.745 | 179.6601 | 224.5751 | 269.4901 | 359.3201 | 538.9802 | 718.6402
|  |  | 0 | 35 | 1.7 | 31.6 | 784.2665 | 0.33732 | 0.050598 | 1.7204 | 3.6867 | 5.4071 | 74.1132 | 111.1698 | 148.2264 | 222.3396 | 296.4527 | 370.5659 | 444.6791 | 592.9055 | 889.3582 | 1185.811
minutes velocity squared / day | 1440 |  | 0 | 42 | 1.7 | 38.6 | 1170.2109 | 0.22607 | 0.033911 | 0.77275 | 1.6559 | 2.4286 | 110.5849 | 165.8774 | 221.1699 | 331.7548 | 442.3397 | 552.9246 | 663.5096 | 884.6794 | 1327.0191 | 1769.3588
|  |  | 0 | 54 | 1.7 | 50.6 | 2010.9003 | 0.13156 | 0.019734 | 0.26169 | 0.56076 | 0.82245 | 190.0301 | 285.0451 | 380.0602 | 570.0902 | 760.1203 | 950.1504 | 1140.1805 | 1520.2407 | 2280.361 | 3040.4813
Peak DHW Primary Flow | 0.26455 | ltr/s | #REF!
Peak CH Primary Flow | 0.039683 | ltr/s