## Precommission
key | property class | plotRef | occupancy | kwDHW | kwCH | floorArea | postCode | emitterTypeCH | connectTypeCH | transferTypeDHW | vStoreDHW | hiuMake | hiuModel | tSetDHW | fBoost | ecoMode | tWarm | minutesWarm | timeWarm1 | timeWarm2 | timeWarm3 | legionella | tSetCH | timeoutPumpCH | returnLimitEnabled | returnLimitTemp
group | property | property | property | property | property | property | property | property | system | system | system | system | system | settings | settings | settings | settings | settings | settings | settings | settings | settings | settings | settings | settings | settings
title | Property Type | Plot Ref | Occupancy | DHW Design Load | Central Heating Design Load | Floor Area | Post Code | Type of Heat Emitter | Type of Central Heating Connection | Type of DHW Connection | Volume of Stored DHW (if present) | HIU Make | HIU Model | DHW Setpoint | Warmup Boost Flow | Keep Warm Mode | Keep Warm Temp | Keep Warm Timeout | Timed Keep Warm 1 | Timed Keep Warm 2 | Timed Keep Warm 3 | Legionalla Protection Enabled | Central Heating Setpoint | Pump Timeout | Return Limit Enabled | Return Limit Temperature
description | A unique reference for a default property type | A unique reference for the property | [7 empty] | Direct = central DHW, instantaneous = plate heat exchanger, coil = connection from netwprk onto a cylinder coil, indirect = fed in turn from secondary system |  |  |  | settings: The flow rate the HIU will draw at tap startup when required; settings: The amount of time that the HIU will keep warm following use; settings: First time for keep warm to start; settings: The duration of heating pump over-run
units |  | Block-Riser-Plot | Beds-People | kW | kW | m2 |  | radiators / underfloor / mixed | direct / indirect | direct / instantaneous / coil / indirect | litres |  |  | °C | lpm | eco / comfort / recirc / timed | °C | minutes | hours:minutes | hours:minutes | hours:minutes | 0/1 | °C | seconds | 0/1 | °C
minimum | [13 empty] | settings: 45; settings: 0; settings: 25; settings: 0; settings: 35; settings: 0; settings: 25
maximum | [13 empty] | settings: 60; settings: 20; settings: 55; settings: 120; settings: 70; settings: 900; settings: 55
default | Standard |  |  | 45 |  |  | CO10 2XW | radiators | indirect | instantaneous | 0 | Thermal Integration | DATA | 52 | 16 | eco | 38 | 0 |  |  |  | 1 | 65 | 300 | 1 | 45
default | Duplex |  |  | 65 |  |  | CO10 2XW | underfloor | indirect | instantaneous | 0 | Thermal Integration | DATA PLUS | 52 | 16 | comfort | 38 | 60 |  |  |  | 1 | 45 | 0 | 0 | 35
plot | Standard | B1-01-01 | 2B3P |  | 2.7 | 75
plot | Duplex | B1-01-02 | 3B5P |  | 4.2 | 95 | [7 empty] | settings: eco
plot | Standard | B1-01-03 | 2B3P |  | 2.6 | 88
plot | Standard | B1-01-04 | 2B3P |  | 2.6 | 88
plot | Standard | B1-01-05 | 2B3P |  | 2.6 | 88 | [7 empty] | settings: 60
plot | Standard | B1-01-06 | 2B3P |  | 2.6 | 90 | [7 empty] | settings: 60
plot | Duplex | B1-01-07 | 3B5P |  | 3.7 | 143
plot | Duplex | B1-01-08 | 3B5P |  | 4.1 | 133
plot | Duplex | B1-01-09 | 3B5P |  | 3.4 | 176
plot | Duplex | B1-01-10 | 4B7P | 20 | 5.5 | 250 |  | mixed |  |  | 150 |  | DATA AMAZON | 55 | 20 | recirc | 45 | 120 | 6:00 | 12:00 | 18:00 |  | 55 |  |  | 45